File Name: UPGRADE.DOC (Host PC)

File Date: 8/30/93

Host Operator Station Revision: I/NET 7700 Revision 2.11

===================================================================

System 7000 Revision 4.XX Upgrades to I/NET 7700 Revision 1.00

The following steps should be followed when upgrading from System

7000 Revision 4.XX to I/NET 7700 Revision 1.00.

1.   If the existing system utilized System 7000 version 4.00 or

higher, the Host software and compatible product specific

firmware may be upgraded to I/NET 7700 software. Older CSI

installations can also be upgraded to I/NET 7700, but may

require additional upgrade steps.  Contact Technical Support

Services for upgrade help if your installation is older than

System 7000 version 4.00.

2.   Before starting any upgrade, BACKUP your existing system

completely!  Before you back-up your system, make sure that

all of your DCU save files are current!  Also make sure that

your Systems Pages, Library Symbols, Docutrend Cells,

Docutrend Reports, Docutrend Extractions and Docutrend Lookup

Tables are current.

3.   Turn off the TAP connected to the computer that you are going

to upgrade.

4.   Install the I/NET 7700 software as outlined in the Operators

Guide.  Answer "Yes" to the prompt asking if this is the first

time you are installing I/NET 7700.

5.   You must now use some of the utility programs included with

the I/NET 7700 software to complete the upgrade of the system.

These programs include:

NETCNV5.EXE: This program is used to upgrade the existing

System 7000 Network Configuration (NETCON) file.  If you

selected the default directories during the I/NET 7700

installation procedure, this program was installed in the

C:\S7000 directory.  You should copy your existing System 7000

NETCON file to this directory (if it is not already there),

and execute this program by typing NETCNV5 and pressing the

[Enter] key.

PGCNV5.EXE: This program is used to upgrade the existing

System 7000 PGGRF, PGDIR, LIBGRF, and LIBDIR files.  If you

selected the default directories during the I/NET 7700

installation procedure, this program was installed in the

C:\S7000\DATA directory.  You should copy your existing System

7000 PGGRF, PGDIR, LIBGRF, and LIBDIR files to this directory

and execute this program by typing PGCNV5 and pressing the

[Enter] key.

Note:  Existing System 7000 graphic pages and symbols were

created in EGA mode.  If you select the VGA mode during the

Setup portion of the installation process, your existing Pages

and symbols may be distorted (especially those with arcs and

fills) and might need to be recreated.

DBCNV45.EXE:  This program is used to upgrade existing System

7000 database save files (DCU????.SAV).  If you selected the

default directories during the I/NET 7700 installation

procedure, this program was installed in the C:\S7000\SAV

directory.  You should copy your System 7000 database save

files, DCU????.SAV, to this directory and execute this program

by typing DBCNV45 followed by LLSS address of the Save file to

be converted and pressing the [Enter] key.  Upon completion of

conversion, the existing System 7000 DCU????.SAV files will be

renamed as DCU????.OLD.

Note:  As a part of this Save file conversion, all reference

points are automatically converted to indirect points.  The

conversion program maps existing reference points onto

resident indirect points as follows:

Reference Points              Indirect Points

1st set of 32 addresses       0009, 0109, ... 3109

2nd set of 32 addresses       0008, 0108, ... 3108

3rd set of 32 addresses       0007, 0107, ... 3107

4th set of 32 addresses       0006, 0106, ... 3106

If there is already a point at a selected address, that

address will be skipped.  Also remember on UCI's, bit offset

addresses 08 and 09 cannot be used if the UC address is

defined as AHU, HPMP, VAV, or GENERAL in the UC Configuration

Editor.

6.   Modify your CONFIG.SYS file by using a DOS text editor such as

EDLIN.  Using your DOS text editor, edit the CONFIG.SYS file

and delete the line DEVICE=C:\S7000\CSITAP.SYS.

7.   Modify your AUTOEXEC.BAT file by using the same technique.

Edit the AUTOEXEC.BAT file and delete the line CSISETUP x.

8.   This step deals with users who had previously stored Docutrend

data in their existing System 7000 installation.  If you have

not utilized Docutrend, you may skip this step.  If you were

previously storing Docutrend data in your System 7000

installation, and you wish to use the same cell data in I/NET

7700, it is important to note that only installations

utilizing version 4.50 or later of the System 7000 software

can transfer their Docutrend files directly to I/NET 7700

software.  If you were utilizing version 4.50 or later of the

System 7000 software, copy your existing Docutrend files to

the I/NET 7700 Docutrend directory.  If you selected the

default directories during the I/NET 7700 installation, these

Docutrend files should be placed in the C:\S7000\RW directory.

Copy the following files to this directory:

RWARCH

RWONLN

RWRMAC

RWRDIR

RWDEMAC

RWDEDIR

RWLTMAC

RWLTDIR

RWGEN

9.   Your PC upgrade is complete.  Now re-boot the PC.  After the

DOS prompt appears, change to the directory which contains the

I/NET 7700 executable program.  If you selected the default

directories during the I/NET 7700 installation, this would be

the C:\S7000 directory.  Type in "I7" and press the [Enter]

key.  Then select item "4" from the menu and follow the

"Setup" configuration procedure as described in the I/NET 7700

Operators Guide.

10.  Before you turn on your TAP you must upgrade all of your

existing S7000 hardware to I/NET 7700 by installing product

specific EPROM(s) or the MIP01 Memory Interface Processor

board.  This upgrade hardware should have been ordered when

your software upgrade was ordered.

If you have any questions concerning any of the above

mentioned information, please call Support Services at

214-323-1111 or FAX at 214-242-0026 for International

Customers.  Thank you for your help in striving to be The Best

There Is.

===================================================================

MIP01 Memory Interface Processor Installation Procedures

I/NET 7700 Revision 1.00 to 1.10 (or higher) Installation

Procedures

Information concerning the installation of the MIP01 is shipped

with each device.  This information is in the form of a Product

Data Sheet (PDS227-04/92).

1.   A MIP01 may be installed on the following products ONLY:

Model 7700 DCU

Model 7740 DCU

Model 7760 UCI

Model 7770 ICI

Model 78010 TAP (metal and plastic enclosure versions)

Model 78015 TAP (metal enclosure version only)

Model 78020 TAP (metal enclosure version only)

Model 78025 TAP (metal and plastic enclosure versions)

Model 78035 TAP (metal and plastic enclosure versions)

Model 78040/41 TAP (metal and plastic enclosure versions)

Model 78050/51 TAP (metal and plastic enclosure versions)

Model 78060/61 TAP (metal and plastic enclosure versions)

Model 7810 TAP

Note:  When installing a MIP01 onto the Model 7770 ICI,

additional 40 pin extenders are required.

2.   Products which may NOT utilize the MIP01 include:

Model 7750 BM

Model 78012 TAP

Model 78013 TAP

Model 78020 TAP (plastic enclosure version only)

Model 78022 TAP

Model 78023 TAP

Model 78032 TAP

Model 78033 TAP

Model 78091, 92 & 93 Bridge TAP

3.   Any product which exists on the same controller LAN where a

MIP01 has been installed or is used to establish

communications with the controller LAN (i.e. Link Taps, dial

taps, etc) which does not have a MIP01 installed, must have

its EPROM changed.  The EPROM installed, must be compatible

with the revision of software installed in the MIP01.

4.   I/NET 7700 Revision 1.10 or later of the software must be

used.  I/NET 7700 Revision 1.00 and 1.10 or higher cannot be

mixed.  Failure to do so will cause problems!

5.   A Host TAP utilizing the MIP01 (7801x) must have its software

downloaded by a PC directly connected to it.  A hardware

address of 0 must be added under Setup in the Shell Menu and

a Host TAP address of 0 must be added to the Network

Configuration Editor before it will appear on the network

summary, allowing it to be saved, and permit software to be

downloaded to it.

6.   Link TAP's utilizing the MIP01 must have their software

downloaded by a PC.  A Link TAP will automatically appear in

the Network Configuration Editor but must be saved in order to

permit software to be downloaded to it.

7.   LAN TAP's utilizing the MIP01 must have their software

downloaded by a PC.  A LAN TAP will automatically appear in

the Network Configuration Editor but must be saved in order to

permit software to be downloaded to it.

8.   While a MIP01 may be transferred to another product after its

initial installation, it was not specifically designed to be

used in this manner.  If you transfer an already installed

MIP01 to another product, you must clear its memory by

removing all of the RAM chips installed in sockets U4 through

U6, followed by re-installing them.

9.   If you are upgrading a System 7000 installation to I/NET 7700

Revision 1.10 (or higher) and using MIP01 product, you cannot

have System 7000 products and I/NET 7700 products on the same

system.  In other words, as you upgrade to I/NET 7700,

Revision 1.10 (or higher) be absolutely sure that you do so in

a manner that ensures NO intermixing of System 7000 or I/NET

Revision 1.00 with I/NET 7700 Revision 1.10 products in the

course of the upgrade.

10.  CAUTION!!!  The MIP01 product should not be installed in

products susceptible to vibration

If you have any questions concerning any of the above

mentioned information, please call Support Services at

214-323-1111 or FAX at 214-242-0026 for International

Customers.  Thank you for your help in striving to be The Best

There Is.

===================================================================

System 7000 Revision 4.XX to I/NET 7700 Revision 2.XX

The following steps should be followed when upgrading from System

7000 Revision 4.XX to I/NET 7700 Revision 2.XX.

1.   If the existing system utilized System 7000 version 4.00 or

higher, the Host software and compatible product specific

firmware may be upgraded to I/NET 7700 software. Older CSI

installations can also be upgraded to I/NET 7700, but may

require additional upgrade steps.  Contact Technical Support

Services for upgrade help if your installation is older than

System 7000 version 4.00.

2.   Before starting any upgrade, BACKUP your existing system

completely!  Before you back-up your system, make sure that

all of your DCU save files are current!    Also make sure that

your Systems Pages, Library Symbols, Docutrend Cells,

Docutrend Reports, Docutrend Extractions and Docutrend Lookup

Tables are current.

3.   Turn off the TAP connected to the computer that you are going

to upgrade.

4.   Install the I/NET 7700 software as outlined in the Operators

Guide.  Answer "Yes" to the prompt asking if this is the first

time you are installing I/NET 7700.

5.   You must now use some of the utility programs included with

the I/NET 7700 software to complete the upgrade of the system.

These programs include:

NETCNV5.EXE: This program is used to upgrade the existing

System 7000 Network Configuration (NETCON) file.  If you

selected the default directories during the I/NET 7700

installation procedure, this program was installed in the

C:\S7000 directory.  You should copy your existing System 7000

NETCON file to this directory (if it is not already there),

and execute this program by typing NETCNV5 and pressing the

[Enter] key.

PGCNV5.EXE: This program is used to upgrade the existing

System 7000 PGGRF, PGDIR, LIBGRF, and LIBDIR files.  If you

selected the default directories during the I/NET 7700

installation procedure, this program was installed in the

C:\S7000\DATA directory.  You should copy your existing System

7000 PGGRF, PGDIR, LIBGRF, and LIBDIR files to this directory

and execute this program by typing PGCNV5 and pressing the

[Enter] key.

Note:  Existing System 7000 graphic pages and symbols were

created in EGA mode.  If you select the VGA mode during the

Setup portion of the installation process, your existing Pages

and symbols may be distorted (especially those with arcs and

fills) and might need to be recreated.

DBCNV46.EXE:  This program is used to upgrade existing System

7000 database save files (DCU????.SAV).  If you selected the

default directories during the I/NET 7700 installation

procedure, this program was installed in the C:\S7000\SAV

directory.  You should copy your System 7000 database save

files, DCU????.SAV, to this directory and execute this program

by typing DBCNV46 followed by LLSS address of the Save file to

be converted and pressing the [Enter] key.  Upon completion of

conversion, the existing System 7000 DCU????.SAV files will be

renamed as DCU????.OLD.

Note:  As a part of this Save file conversion, all reference

points are automatically converted to indirect points.  The

conversion program maps existing reference points onto

resident indirect points as follows:

Reference Points              Indirect Points

1st set of 32 addresses       0009, 0109, ... 3109

2nd set of 32 addresses       0008, 0108, ... 3108

3rd set of 32 addresses       0007, 0107, ... 3107

4th set of 32 addresses       0006, 0106, ... 3106

If there is already a point at a selected address, that

address will be skipped.  Also remember on UCI's, bit offset

addresses 08 and 09 cannot be used if the UC address is

defined as AHU, HPMP, VAV, or GENERAL in the UC Configuration

Editor.

6.   Modify your CONFIG.SYS file by using a DOS text editor such as

EDLIN.  Using your DOS text editor, edit the CONFIG.SYS file

and delete the line DEVICE=C:\S7000\CSITAP.SYS.

7.   Modify your AUTOEXEC.BAT file by using the same technique.

Edit the AUTOEXEC.BAT file and delete the line CSISETUP x.

8.   This step deals with users who had previously stored Docutrend

data in their existing System 7000 installation.  If you have

not utilized Docutrend, you may skip this step.  If you were

previously storing Docutrend data in your System 7000

installation, and you wish to use the same cell data in I/NET

7700, it is important to note that only installations

utilizing version 4.50 or later of the System 7000 software

can transfer their Docutrend files directly to I/NET 7700

software.  If you were utilizing version 4.50 or later of the

System 7000 software, copy your existing Docutrend files to

the I/NET 7700 Docutrend directory.  If you selected the

default directories during the I/NET 7700 installation, these

Docutrend files should be placed in the C:\S7000\RW directory.

Copy the following files to this directory:

RWARCH

RWONLN

RWRMAC

RWRDIR

RWDEMAC

RWDEDIR

RWLTMAC

RWLTDIR

RWGEN

9.   Your PC upgrade is complete.  Now re-boot the PC.  After the

DOS prompt appears, change to the directory which contains the

I/NET 7700 executable program.  If you selected the default

directories during the I/NET 7700 installation, this would be

the C:\S7000 directory.  Type in "I7" and press the [Enter]

key.  Then select item "4" from the menu and follow the

"Setup" configuration procedure as described in the I/NET 7700

Operators Guide.

10.  Before you turn on your TAP you must upgrade all of your

existing S7000 hardware to I/NET 7700 by installing product

specific EPROM(s) or the MIP01 Memory Interface Processor

board.  Using the Software Restore editor, software must be

downloaded to all 7716, 7718, 7780 DCU's or any devices with

MIP's installed. See MIP installation instructions above. Any

upgrade hardware should have been ordered when your software

upgrade was ordered.

If you have any questions concerning any of the above

mentioned information, please call Support Services at

214-323-1111 or FAX at 214-242-0026 for International

Customers.  Thank you for your help in striving to be The Best

There Is.

==================================================================

I/NET 7700 Revision 1.XX to I/NET 7700 Revision 2.XX

The following steps should be followed when upgrading from I/NET

7700 Revision 1.XX to I/NET 7700 Revision 2.XX.

1.   Before starting any upgrade, BACKUP your existing system

completely!  Before you back-up your system, make sure that

all of your DCU save files are current!  Also make sure that

your Systems Pages, Library Symbols, Docutrend Cells,

Docutrend Reports, Docutrend Extractions and Docutrend Lookup

Tables are current.

2.   Turn off the TAP connected to the computer that you are going

to upgrade.

3.   Install the I/NET 7700 software as outlined in the Operators

Guide.  Answer "No" to the prompt asking if this is the first

time you are installing I/NET 7700.

4.   You must now use the Database convert program (DBCNV46.EXE)

included with the I/NET 7700 software to complete the upgrade

of the system.  This program is used to upgrade existing I/NET

7700 Revision 1.XX (or System 7000 Rev 4.XX) database save

files (DCU????.SAV).  If you selected the default directories

during the initial I/NET 7700 installation procedure, this

program was installed in the C:\S7000\SAV directory.  Your

I/NET 7700 database save files should also be located in this

directory. Execute this program by typing DBCNV46 followed by

LLSS address of the Save file to be converted and pressing the

[Enter] key.  Upon completion of conversion, the existing

I/NET 7700 Revision 1.XX save files will be renamed as

DCU????.OLD.

5.   Your PC upgrade is complete.  Now re-boot the PC.  After the

DOS prompt appears, change to the directory which contains the

I/NET 7700 executable program.  If you selected the default

directories during the initial I/NET 7700 installation, this

would be the C:\S7000 directory.  Type in "I7" and press the

[Enter] key.

6.   Before you turn on your TAP you must upgrade all of your

existing I/NET 7700 Revision 1.XX hardware to I/NET 7700

Revision 2.XX by installing product specific EPROM(s) or the

MIP01 Memory Interface Processor board.  Using the Software

Restore editor, software must be downloaded to all 7716, 7718,

7780 DCU's or any devices with MIP's installed.  See MIP

installation instructions above.  Any upgrade hardware should

have been ordered when your software upgrade was ordered.

If you have any questions concerning any of the above

mentioned information, please call Support Services at

214-323-1111 or FAX at 214-242-0026 for International

Customers.  Thank you for your help in striving to be The Best

There Is.

===================================================================

I/NET 7700 Revision 2.00 to I/NET 7700 Revision 2.XX

The following steps should be followed when upgrading from I/NET

7700 Revision 2.00 to I/NET 7700 Revision 2.XX.

1.   Before starting any upgrade, BACKUP your existing system

completely!  Before you back-up your system, make sure that

all of your DCU save files are current!  Also make sure that

your Systems Pages, Library Symbols, Docutrend Cells,

Docutrend Reports, Docutrend Extractions and Docutrend Lookup

Tables are current.

2.   Turn off the TAP connected to the computer that you are going

to upgrade.

3.   Install the I/NET 7700 software as outlined in the Operators

Guide.  Answer "No" to the prompt asking if this is the first

time you are installing I/NET 7700.

4.   Your PC upgrade is complete.  Now re-boot the PC.  After the

DOS prompt appears, change to the directory which contains the

I/NET 7700 executable program.  If you selected the default

directories during the initial I/NET 7700 installation, this

would be the C:\S7000 directory.  Type in "I7" and press the

[Enter] key.

If you have any questions concerning any of the above

mentioned information, please call Support Services at

214-323-1111 or FAX at 214-242-0026 for International

Customers.  Thank you for your help in striving to be The Best

There Is.

===================================================================